## Maintenance Work Order
MAINTENANCE WORK ORDER
[Facility / Property Name] • Maintenance Department
REQUEST |  | ASSET / LOCATION
WO Number | MWO-0582 | Building | Main Office
Date Requested | 2026-11-03 | Floor / Room | 2nd floor, Room 214
Requested By | Front desk – K. Ali | Asset / Equipment | Rooftop AC unit RTU-2
Priority | High | Asset ID | HVAC-0214
Type | Corrective | Assigned To | M. Fischer (HVAC)
PROBLEM DESCRIPTION
Room 214 not cooling; unit runs but blows warm air. Reported 3 times this week.
WORK PERFORMED
Cleaned condenser coil, replaced failed capacitor, checked refrigerant pressure (normal). Unit cooling to 72°F.
Part No. | Part Description | Qty | Cost
CAP-45-5 | Run capacitor 45/5 MFD | 1
FLT-2025 | Air filter 20x25x2 | 2
Date | Time Start | Time Finish | Hours
2026-11-04 | 9:15 | 11:45
2026-11-05 | 8:30 | 9:30
Follow-up needed? ☐ Yes ☐ No |  | Total labor hours
Downtime (hours): 26 |  | Labor rate | 55
Root cause: Failed capacitor (age) |  | Labor cost
Parts cost
TOTAL COST
COMPLETION SIGN-OFF
Technician: ____________________ |  | Supervisor: ____________________
Date completed: ____________ |  | Requester notified: ☐